[image: ]Highways and Engineering Service - Economy and Environment
Drainage Consultation on Application – 25/00118/DOC - RBC Town Hall -Broadfield Slopes, Rochdale OL16 1NJ
LLFA Consultation Response on behalf of Head of Highways and Engineering
Date of Response: 8th April 2025
Location & Proposed Development
RBC Town Hall Broadfield Slopes, Rochdale OL16 1NJ
Submission of details to comply with conditions 3 (tree protection), 4 (CEMP), 5 (Phase II habitat survey), 6 (archaeological WSI), 7 (invasive species), 8 (contamination), 9 (drainage), 10 (fixtures and fittings), 11 (materials samples), 12 (repairs methodology - fountain), 13 (repairs methodology - market cross), 14 (replacement obelisk), 15 (pond works), 16 (lighting scheme), 17 (planting plan) and 18 (bird nesting season) on planning permission 23/01393/FUL Landscaping and planting scheme to Broadfield Park Slopes (Grade II registered park)
Documents Reviewed
· Planning Decision Notice (23/01393/FUL)
· Phase 2 South Slopes Infrastructure, drawing no. 30217 / 6002, Rev P10
Drainage & Flood Officer Comments
1. The enabling works drg indicates the western land drainage outfall is to be discharged to combined sewers. This is not acceptable in principle. It is not acceptable to discharge land drainage to public sewers.  
2. The eastern outfall is noted to be discharged into a previous phase drainage. Please confirm the ultimate outfall point for this drainage. If it is again to public sewers then this is also unacceptable.
3. There is no drainage strategy report to support the layout. It is unclear if infiltration options have been assessed.
4. It is unclear what areas are draining to the ponds and swales as they appear to be located in uphill locations whereas they may be more effective within the lower sections.
5. The proposal should be supported by a maintenance plan explaining how the surface water scheme will be maintained and managed after completion.

Drainage & Flood Officer Summary:
I. The proposed layout should be supported by a drainage strategy to explain the options selected.
II. Discharge of land drainage to public sewers is not acceptable in principle.
III. Provide a Maintenance document for the SuDS components used within the proposed drainage scheme. 
IV. The above points should be addressed before the application is approved. 
Consultation by Keith Mealey
Drainage & Flooding Officer
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