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Drainage Consultation on Application – 25/00128/DOC - Riverside Motors Todmorden Road Littleborough Rochdale OL15 9EG
LLFA Consultation Response on behalf of Head of Highways and Engineering
Date of Response: 15th May 2025
Location & Proposed Development
Riverside Motors Todmorden Road Littleborough Rochdale OL15 9EG
Submission of details to comply with conditions 4 (site investigation) and 5 (drainage schemes) on planning permission 23/01374/FUL
Documents Reviewed
23/01374/FUL
· Microdrainage Calculations (1 In 1, 1 In 30, 1 In 100)
· Phase 2 Site Investigation And Geo-Environmental Appraisal 
25/00128/DOC
· Drainage plan & details dwg-tjba-green-riverside business park-151221 Rev 0
· Microdrainage Calculations (1 in 1, 1 in 30, 1 in 100)
· Phase 2 Site Investigation and Geo-environmental appraisal 
· 
Drainage & Flood Officer Comments
Condition 5 of 23/01373/FUL requires the drainage scheme to incorporate. 
(i) A restricted rate of surface water discharge to the adjacent watercourse to 5l/s, attenuation storage within the site, and an appropriately specified fuel interceptor.
(ii) Construction details for permeable paving including kerbing and cross-section of open graded sub-base, if this type of paving forms part of the sustainable drainage system.
(iii) Levels of the proposed drainage systems including proposed ground and finished floor levels in mAOD.
(iv) The background calculations of the MicroDrainage model or any other software or calculations that have been used for the drainage design.
(v) Provision of a short Maintenance Document explaining how the surface water scheme will be maintained and managed after completion. This should include an As-Built drainage plan of the site.

1. The applicant has provided an updated drainage plan indicating the drainage arrangements of the scheme. 
· Surface water discharge restricted to 5 l/s to the adjacent watercourse
· Attenuation storage 
· Shown a petrol interceptor included on the drainage scheme.

2. The proposal has included Levels of the proposed drainage systems including proposed ground and finished floor levels in mAOD on the drainage plan drawing. However, the FRA identifies a minimum FFL of 145.95m. However, the drainage plan indicates lower FFLs. Please clarify.




3. The proposal has included the appropriate micro-drainage calculations with the correct climate change events used to support their drainage scheme.

4. The proposal has not yet indicated a maintenance plan for the SuDS components used within the drainage scheme. This is required to discharge condition 5. 

Drainage & Flood Officer Summary:
I. Clarify / confirm that FFLs are 145.95 minimum in accordance with the FRA.
II. The condition requires the submission of a maintenance plan.
III. The above points should be addressed before the application is approved. 

Consultation by Keith Mealey
Drainage & Flooding Officer
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