## Fourth wall
Condition Report: Castle Inn, 111 Manchester Road, Rochdale OL11 4HY Fourth Wall reference: 24.377 Property: Castle Inn, Rochdale OL11 4HY Client specific reference: N/A Date: 24-Jul-24
Item | Element | Location | Defect Description | Recommended Works | Condition | Priority | Quantity | Unit
1 | External Building Fabric
1.1 | Roof Areas
Generally
1.1.1 | Access | Throughout | The provision of safe access for undertaking roof works. |  |  |  | 1 | item
1.1.2 | Rainwater goods | Throughout | The gutters are subject to a build up of silt and debris. | Pressure clean, including associated downpipes to ensure free flowing and operational. | C | 1 | 316 | m
1.1.3 | Rainwater goods - downpipes | Throughout | The decorative finish to previously decorated downpipes is peeling to isolated locations. | Prepare and decorate. | C | 2 | 3 | nr
1.1.4 | Slates | Throughout | There are numerous slipped, cracked or poorly repaired slates throughout the roof coverings. | Replace. | D | 1 | 70 | nr
Main roof
1.1.5 | Slates | Throughout | The slate roof covering is dirt marked with a build up of detritus, staining and moss/vegetation growth. | Clean, including verge and ridge details. | C | 2 | 350 | m2
1.1.6 | Lead flashings | Throughout | The lead flashings are approaching the end of their serviceable life. | Replace lead flashings, including valley gutters etc. | D | 1 | 45 | m
1.1.7 | Chimneys (6Nr) | Throughout | There are numerous cracked, washed out and degraded mortar joints to the chimneys. | Rake out and repoint. | D | 1 | 1 | item
1.1.8 | Ridge and hip tiles | Throughout | There are numerous cracked, washed out and degraded mortar joints to the ridge and hip tiles. | Rake out and repoint. | C | 1 | 51 | m
Central valley flat roof
1.1.9 | Felt roof | Throughout | The flat felt roof appears to be in fair condition commensurate with age, however due to restricted access, we recommend a thorough inspection once access is obtained. | Allow to inspect and consideration for replacement in the medium term with a new, single ply EPDM roof covering. | B | 3 | 6 | m2
1.2 | Elevations
Generally
1.2.1 | Brickwork | All elevations | The brickwork throughout the elevations is dirt marked. Furthermore, there are isolated areas of graffiti and residual paint spills to elevations. | Undertake a DOFF steam clean brickwork and to remove imperviable paint, allowing the historic brickwork to breathe as intended. | C | 2 | 375 | m2
1.2.2 | Joinery surfaces | Throughout | The decorative finish to the joinery surfaces throughout is generally peeling and in poor condition. | Redecorate, including trusses, struts, doors, fascia's, soffits, etc. with a suitable permeable timber grade external paint to prevent deterioration and improve aesthetics. | C | 3 | 1 | item
1.2.3 | Joinery surfaces | Throughout | There are isolated redundant fixings throughout the external joinery surfaces. | Remove and undertake isolated patch repair with linseed oil putty, prior to redecoration. | B | 3 | 1 | item
Front Elevation (1)
1.2.4 | Brickwork | Front elevation | There are 5 no. isolated redundant penetrations to brickwork. | Carefully cut out and replace affected brickwork with a like-for-like brick and repoint. | C | 2 | 1 | item
1.2.5 | Stonework | Front elevation | There is an isolated redundant fixing to the low-level stonework. | Carefully remove fixing and patch repair with a suitable lime mortar mix, to prevent further deterioration. | C | 2 | 1 | item
1.2.6 | Stonework | Front elevation | There are isolated scars to the stone cill to the left side windows. | Undertake isolated plastic lime mortar repair to prevent further deterioration. | C | 2 | 1 | item
1.2.7 | Stonework | Front elevation | The underside of the stonework to the porch area is spalling. | Defrass stone, and consider longer term plastic lime mortar repairs. | B | 2 | 1 | m2
1.2.8 | Mortar joints | Front elevation | There are isolated missing mortar joints at low level to stonework, including to the porch area. | Rake out and repoint using a lime mortar mix. | D | 2 | 10 | m
1.2.9 | Plaster panels | Front elevation | There are isolated cracks to the plaster panels at high level. | Tap test and undertake isolated repairs to prevent further deterioration. | C | 2 | 1 | item
2010-01-02 | Plaster panels | Front elevation | The decorative finish to the plaster panels at high level is beginning to deteriorate and peel in locations. | Prepare and redecorate. | C | 3 | 1 | item
2011-01-02 | Timber trusses and joinery surfaces | Front elevation | The decorative finish to the mock Tudor trusses, and associated joinery is beginning to deteriorate and peel in locations. | Prepare and redecorate. | C | 3 | 1 | item
2012-01-02 | Timber trusses and joinery surfaces | Front elevation | There are isolated splits to the timber struts, trusses etc. This is typical of a building of this age, however we recommend the following remedial works to prevent rots and further deterioration. | Carefully fill splits and cracks with a linseed oil putty and allow to redecorate isolated areas. | C | 2 | 1 | item
2013-01-02 | Timber boarding | Front elevation | There is a missing section of boarding above the right side first floor window. | Replace boarding to prevent potential water ingress and vermin entry point. | D | 1 | 2 | m
2014-01-02 | Timber barge boards | Front elevation | There are isolated sections of rot to the barge boards. | Carefully cut back sections of rot to the appropriate distance, treat with a suitable fungicide and splice repair. | D | 1 | 10 | m
2015-01-02 | Timber soffit | Front elevation | There is a redundant lead pipe to the underside of the soffit. | Remove and undertake replace penetrated section of timber boarding to improve aesthetics. | B | 3 | 1 | item
Right side elevation (2 & 4)
2018-01-02 | Mortar joints | Right elevation | There are isolated missing mortar joints at low level adjacent to the left side downpipe. | Rake out and repoint using a suitable lime mortar mix. | C | 2 | 1 | item
2019-01-02 | Brickwork | Right elevation | There are 2 no. isolated chipped bricks. | Cut out and replace. | B | 3 | 1 | item
2020-01-02 | Timber trusses and joinery surfaces | Right elevation | There are isolated splits to the timber struts, trusses etc. This is typical of a building of this age, however we recommend the following remedial works to prevent rots and further deterioration. | Carefully fill splits and cracks with a linseed oil putty and allow to redecorate isolated areas. | C | 2 | 1 | item
2021-01-02 | Plaster panels | Right elevation | There are isolated cracks to the plaster panels at high level to 10 no. panels. | Tap test and undertake isolated repairs to prevent further deterioration. | C | 3 | 1 | item
Front elevation (3)
2024-01-02 | Stonework | Front elevation | There are crude cement mortar repairs to the associated stonework. | Carefully rake out and repoint with a suitable lime mortar mix to prevent further deterioration. | C | 2 | 5 | m
2025-01-02 | Stonework | Front elevation | There are isolated sections of spalling stone work to the porch area. | Defrass stone, and undertake plastic lime mortar repairs. Consideration should be made for long term indent repairs. | C | 2 | 2 | m2
2026-01-02 | Stonework | Front elevation | There is cracking to the stone work and furthermore, stonework has been over painted. |  |  |  | 1 | item
2027-01-02 | Plaster panels | Front elevation | There are isolated cracks to the plaster panels at high level to 8 no. panels. | Tap test and undertake isolated repairs to prevent further deterioration. | C | 3 | 1 | item
Rear elevation (5)
2032-01-02 | Mortar joints | Rear elevation | There are missing mortar joints to the off shut/out rigger. | Rake out and repoint using a lime mortar mix. | D | 2 | 5 | m
2033-01-02 | Plaster panels | Rear elevation | There are isolated cracks to the plaster panels at high level, however appear to be stable where tested. | Tap test and undertake isolated repairs to prevent further deterioration. | C | 3 | 1 | item
2034-01-02 | Plaster panels | Rear elevation | There is poor cement repairs surrounding the soil and vent pipe protruding the elevation. | Hack off, patch repair and redecorate. | C | 3 | 1 | m2
2035-01-02 | Plaster panels | Rear elevation | There is a missing section of pipework to the soil and vent pipe. Furthermore a section has been removed from the elevation and the redundant penetration filled with expanding foam. | Reconnect all waste water drainage runs into the soil and vent pipe, remove expanding foam and undertake isolated patch repair and decorate. | D | 1 | 1 | item
2036-01-02 | Timber trusses and joinery surfaces | Rear elevation | There is a missing section of timber to the soffit/fascia. | Replace. | D | 2 | 1 | m
2037-01-02 | Drainage | Rear elevation | The lead soil and vent pipe has been impact damaged and crimped. | Reinstate with new to ensure operational. | D | 1 | 1 | item
Rear elevation (6)
2041-01-02 | Cabling | Rear elevation | There are numerous assumed redundant cabling. | Remove back to source and repair redundant penetration. | D | 2 | 1 | item
Rear elevation (7)
2042-01-02 | Brickwork | Rear elevation | There are circa 40 no. penetrated bricks. | Carefully cut out and replace brickwork with like- for-like brickwork. | D | 2 | 1 | item
2043-01-02 | Stone work | Rear elevation | There is isolated degradation to the stonework, including to quoins and above windows. | Defrass and undertake isolated plastic lime mortar repairs in the short term. Consideration should be made to undertake long term dutchman indent repairs. | C | 2 | 1 | item
2044-01-02 | Mortar joints | Rear elevation | There are isolated missing mortar joints throughout the elevation. | Rake out and repoint using a lime mortar mix. | D | 2 | 1 | item
2045-01-02 | Rainwater goods - downpipe | Rear elevation | The cast iron downpipe and associated hopper is corroded. | Prepare and treat with a suitable zinc rich primer prior to redecoration. NB: Cost for redecoration allowed for within general item. | D | 1 | 1 | item
2046-01-02 | Timber soffit | Rear elevation | The underside of the soffit is stained, with likely sections of rot present. | Undertake provisional replacement of affected panels (10 no.) | C | 2 | 1 | item
2047-01-02 | Timber barge boards | Rear elevation | There are isolated sections of rot to the barge boards. | Carefully cut back sections of rot to the appropriate distance, treat with a suitable fungicide and splice repair. | D | 1 | 1 | item
2049-01-02 | Corrosion to the metal plates externally – allow to replace/treat corrosion. | [5 empty] | 1 | item
2050-01-02 | Furthermore, allow to undertake isolated splice repairs to frame. | [5 empty] | 1 | item
Left side elevation (8)
2051-01-02 | Brickwork | Left elevation | There are 8 no. redundant penetrations to the brickwork. | Carefully cut out and replace brickwork with like- for-like brickwork. | D | 2 | 1 | item
2052-01-02 | Stonework | Left elevation | The corner stone to the lower left side of the timber entrance door has significantly moved. | Inspect with a qualified structural engineer and re- set. | D | 2 | 1 | item
2053-01-02 | Mortar joints | Left elevation | There are isolated missing mortar joints throughout the elevation. | Rake out and repoint using a lime mortar mix. | D | 2 | 1 | item
2054-01-02 | Timber soffit | Left elevation | The underside of the soffit is stained, with likely sections of rot present. | Undertake provisional replacement of affected panels (10 no.) | C | 2 | 1 | item
2055-01-02 | Timber trusses and joinery surfaces | Left elevation | There are isolated sections of rot to the timber struts, trusses etc. | Undertake isolated splice repairs to prevent further deterioration prior to redecoration. NB: Cost for redecoration allowed for in general items. | C | 2 | 1 | item
1.3 | Hardstandings & Outbuildings
Generally
1.3.1 | Hardstandings | Throughout | The hardstandings are generally dirt marked with a build up of litter, dirt, moss and detritus. | Allow to pressure clean and remove build up of litter. | B | 1 | 1 | item
Rear hardstandings
1.3.5 | Brickwork boundary wall | Rear boundary | There are numerous missing mortar joints to the rear boundary wall. | Rake out and repoint. | D | 1 | 1 | item
1.3.6 | Brickwork boundary wall | Rear boundary | There is an isolated oversailing section of brickwork to the retaining wall. | Inspect with a suitably qualified structural engineer and undertake recommended remedial works. | C | 2 | 1 | item
1.3.7 | Concrete hardstandings | Concrete slab | There are numerous cracks, fissures and degraded sections to the hardstandings. | Undertake epoxy resin repairs in the short term to prevent further deterioration. NB: Consideration should be made to install a tarmacadam wearing course in the long term (cost allowed). | C | 2 | 1 | item
2010-01-03 | Gate | Pre-finished vehicular entrance gate | The entrance gate is corroded in isolated locations. | Allow to treat corrosion with a zinc rich primer and re-spray. | C | 2 | 1 | item
2011-01-03 | Brickwork | Brick pillars to gate | There are numerous missing mortar joints with a build up of minor efflorescence. | Rake out and repoint and defrass efflorescence. | D | 1 | 1 | item
1.4 | Internals
Ground floor
Main foyer
2010-01-04 | Plaster | Internal wall (historic fire hearth) | There are isolated damaged sections of plasterboard. | Undertake isolated repairs. | B | 2 | 1 | item
2011-01-04 | Plaster | Column & beam fire boarding | There are isolated penetrations to columns and high level beams to investigate the structure. | Undertake isolated patch repairs. | B | 2 | 1 | item
2012-01-04 | Framework | Throughout | The framework has isolated corrosion present. | Treat with a suitable zinc rich primer. | C | 2 | 1 | item
2013-01-04 | Floor covering | Serving the basement staircase lobby. | There are isolated sections of extensive rot to the parquet floor slats. | Replace sections. | C | 1 | 1 | item
Staircase and lobby
2026-01-04 | Plasterwork | Staircase reveals | The plaster finish has been hacked off to the staircase reveals. | Replaster. | C | 1 | 1 | item
2028-01-04 | Joinery surfaces | To staircase | There is a rotten section to the intermediate landing on the staircase. | Undertake repairs following issue of timber report to prevent trip or falling hazard. | D | 1 | 1 | item
First Floor
Generally
2033-01-04 | Plaster | Throughout | There are isolated penetrated/impact damaged sections of plaster, with isolated build ups of efflorescence throughout the first floor walls. | Should the walls remain in their current configuration, allow to remove efflorescence and undertake isolated patch repairs. | C | 2 | 1 | item
2039-01-04 | Framework | First floor | The frame is exhibiting signs of early on-set corrosion. | Treat with a suitable zinc rich primer to prevent further deterioration. | D | 2 | 1 | item