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Drainage Consultation on Application – 24/00927/FUL - Hillside And Land To South Of Stable Hills, Chadwick Hall Road, Rochdale, OL11 4DJ
LLFA Consultation Response on behalf of Head of Highways and Engineering
Date of Response: 29th April 2025
Location & Proposed Development
Hillside And Land To South Of Stable Hills , Chadwick Hall Road, Rochdale, OL11 4DJ
Erection of 2no. three storey detached dwellings and associated works including excavation and landscaping, creation of new vehicular access and car parking.
Documents Reviewed
· Design & Access Statement – September 2017
· Technical Note – 04 August 2017
· Proposed Site Plan
· Existing Site Plan
Drainage & Flood Officer Comments
1. No drainage information has been provided to support the application. The Technical note focusses on highways / access issues.

2. The proposed development consists of two new dwellings on sloping land. The site is less than 1 hectare, is not within a designated flood risk zone and does not appear to have any local flood risk features / issues. Therefore, Flood Risk Assessment (FRA) is not required. However, the applicant must still demonstrate adequate surface and foul water drainage provisions to ensure effective water management.

3. The aim should be to discharge surface run off as high up the following hierarchy of drainage options as reasonably practicable: The ordered drainage techniques to be assessed with the aim to reduce or omit lower techniques:
· Control at Source (Infiltration / Recycling)
· On Site Treatment (Basins, Swales, Rain gardens, Tree pits)
· Local Treatment (Adoptable Ponds, Basins, Swales etc)
· Regional Treatment (ditto usually to a larger scale)
· Discharge to Watercourses / Bodies
· Discharge to SW Sewers
· Discharge to Combined Sewers

4. If infiltration is proposed, the applicant must provide BRE 365 infiltration test results to confirm the suitability of the ground conditions for this method

5. If the development intends to connect to an existing watercourse or sewer, the applicant must provide evidence of discharge permissions from the relevant authority.
6. It is unclear if there are any watercourses close to the site. However, there are public surface water sewers in Links View and there is a potential public footpath route to between the site and Links View.

7. The developer should confirm that post-development runoff will not increase flood risk to adjacent properties, either by maintaining pre-development runoff rates or through the use of attenuation measures.

8. Although this is a small-scale development, a 45% climate change allowance should be applied to ensure that the drainage system is resilient to extreme rainfall events.

9. Foul drainage arrangements should also be clarified.

Drainage & Flood Officer Summary:
I. The application should be supported with an acceptable drainage strategy / proposal
II. It is not considered appropriate to apply conditions to a non-existent strategy or a strategy which is not acceptable in principle.
III. The above points should be addressed before the application is approved. 

Consultation by Keith Mealey
Drainage & Flooding Officer
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