# Highways and Engineering Service - Economy and Environment

# Drainage Consultation on Application – 24/00927/FUL - Hillside And Land To South Of Stable Hills, Chadwick Hall Road, Rochdale, OL11 4DJ

LLFA Consultation Response on behalf of Head of Highways and Engineering

Date of Response: 29th April 2025

Location & Proposed Development

Hillside And Land To South Of Stable Hills , Chadwick Hall Road, Rochdale, OL11 4DJ

Erection of 2no. three storey detached dwellings and associated works including excavation and landscaping, creation of new vehicular access and car parking.

Documents Reviewed

- Design & Access Statement – September 2017

- Technical Note – 04 August 2017

- Proposed Site Plan

- Existing Site Plan

Drainage & Flood Officer Comments

- No drainage information has been provided to support the application. The Technical note focusses on highways / access issues.

- The proposed development consists of two new dwellings on sloping land. The site is less than 1 hectare, is not within a designated flood risk zone and does not appear to have any local flood risk features / issues. Therefore, Flood Risk Assessment (FRA) is not required. However, the applicant must still demonstrate adequate surface and foul water drainage provisions to ensure effective water management.

- The aim should be to discharge surface run off as high up the following hierarchy of drainage options as reasonably practicable: The ordered drainage techniques to be assessed with the aim to reduce or omit lower techniques:

- Control at Source (Infiltration / Recycling)

- On Site Treatment (Basins, Swales, Rain gardens, Tree pits)

- Local Treatment (Adoptable Ponds, Basins, Swales etc)

- Regional Treatment (ditto usually to a larger scale)

- Discharge to Watercourses / Bodies

- Discharge to SW Sewers

- Discharge to Combined Sewers

- If infiltration is proposed, the applicant must provide BRE 365 infiltration test results to confirm the suitability of the ground conditions for this method

- If the development intends to connect to an existing watercourse or sewer, the applicant must provide evidence of discharge permissions from the relevant authority.

- It is unclear if there are any watercourses close to the site. However, there are public surface water sewers in Links View and there is a potential public footpath route to between the site and Links View.

- The developer should confirm that post-development runoff will not increase flood risk to adjacent properties, either by maintaining pre-development runoff rates or through the use of attenuation measures.

- Although this is a small-scale development, a 45% climate change allowance should be applied to ensure that the drainage system is resilient to extreme rainfall events.

- Foul drainage arrangements should also be clarified.

Drainage & Flood Officer Summary:

- The application should be supported with an acceptable drainage strategy / proposal

- It is not considered appropriate to apply conditions to a non-existent strategy or a strategy which is not acceptable in principle.

- The above points should be addressed before the application is approved.

Consultation by Keith Mealey

Drainage & Flooding Officer

keith.mealey@rochdale.gov.uk