| Planning Application Review |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Planning Application |  |  |  | Minor extensions and infills to facilitate the re-organisation and refurbishment of internal spaces and to increase bedroom capacity from 23 to 32 (29 standard, 2 category 3 and one emergency room), along with replacement of windows and doors, resurfacing of external areas, minor landscape works, new access gates and new and upgraded external lighting. |  |  |
| Application Reference |  |  |  | PL/2025/1215 |  |  |
| Applicant |  |  |  |  |  |  |
| Lighting Type |  |  |  | Outdoor Lighting |  |  |
| Our Reference |  |  |  | RMBC 30-02-2025 1215-01 (23/02/2026) |  |  |
| Documents Reviewed |  |  |  |  |  |  |
| - Proposed External Lighting-Illuminance Layout - Proposed External Lighting Layout |  |  |  |  |  |  |
| Lighting Requirements |  |  |  |  |  |  |
| For any proposed external lighting, other than that shall be adopted by the Local Authority shall be submitted to the Local Authority Planning Department for review. The following information is required to ensure the proposed non-adoptable lighting design protects residents and amenities against intrusive light. |  |  |  |  |  |  |
| 1. |  | A full lighting design, calculations, and detailed layout - providing details of lanterns, angle of lanterns, maintenance factors, mounting heights, exact locations of lanterns etc. |  |  |  |  |
| 2. |  | Confirmation of lighting standards the private area has been lit to (BS5489, CIBSE etc.) |  |  |  |  |
| 3. |  | Calculations showing compliance with ILE guidelines (GN01) for the control of intrusive lighting to Environmental Zone E3 |  |  |  |  |
| 4. |  | Lux plots showing light spill onto surrounding areas to include 10, 5 and 1 lux levels |  |  |  |  |
| 5. |  | Source Intensity of lanterns should be considered for the proposed installation to ensure compliance with the requirements of GN01. |  |  |  |  |
| 6. |  | All lighting calculations showing light spill and obtrusive light should be for worst case scenario, i.e., when the installation is first operational. |  |  |  |  |
| 7. |  | If any complaints are received, the Maintaining Body should consider the fitting of shields to the lanterns in line with the Institute of Lighting Professionals (ILP) “Guidance notes for the reduction of obtrusive light” - Environmental Zones |  |  |  |  |
| Comments |  |  |  |  |  |  |
| 1. | Detailed lighting layout is to be provided. The layout shall clearly identify the column heights and locations and the lantern aiming direction. The layout shall include for a detailed descriptive key providing details of the lanterns and their tilts from the horizontal, and any back light shields to be fitted. The layout shall also clearly show the lux lines for 1, 5 and 10lux showing the spill from the courts. |  |  |  |  |  |
| 2. | Lighting standards and the selection class shall be confirmed of what the areas are to be lit to. |  |  |  |  |  |
| 3. | If there are any curfew hours applied to the site for usage, it should be noted on Layout. Switching times of outdoor lighting to be included on the layout. |  |  |  |  |  |
| 4. | Lux lines have been shown but need to be shown clearly as stated above. |  |  |  |  |  |
| 5. | Calculations to be provided |  |  |  |  |  |
| 6. |  |  |  |  |  |  |
| Requested Lighting Planning Conditions |  |  |  |  |  |  |
| As part of the design submission the Developer shall provide the following information so that a design review can be carried out: |  |  |  |  |  |  |
| On behalf of Street Lighting Team |  |  |  |  |  |  |
| Prepared by |  |  | Philip Beveridge |  | Approved by | Andy Ashton FIHE |
| Position |  |  | Joint Authority PFI Design Engineer |  | Position | Joint Authority PFI Project Manager |
| Date |  |  |  |  | Date |  |
| Signed |  |  |  |  | Signed |  |