# Highways and Engineering Service - Economy and Environment

# Drainage Consultation on Application – PL/2026/0112 – Birch Business Park, Whittle Lane, Heywood, Rochdale, OL10 2SX

LLFA Consultation Response on behalf of Head of Highways and Engineering

Date of Response 28th May 2026

Location & Proposed Development

Birch Business Park, Whittle Lane, Heywood, Rochdale, OL10 2SX

Section 73 application to vary conditions 2 (Approved Plans), 3 (Invasive Species), 4 (Tree Protection(, 6 (Drainage Strategy), 8 (CMP), 9 (Materials), 11 (Landscaping), 13 (Cycle Parking), 14 (External Lighting), 16 (EV Charging Points), 19 (Acoustic Barrier) and 20 (Energy Statement) of planning permission 24/00453/VRCON.

Documents Reviewed

25-021-IL Response to LLFA Objection 1

Previous LLFA comments 28/03/26

PL/2026/0112

- Flood Risk Assessment

- Drainage Strategy

24/00453/VRCON to original app. 22/01148/FUL

- Location Plan

- Proposed Site Plan

- Ground Investigation dated 30/03/2022

Drainage & Flood Officer Comments

- Previous LLFA comments challenged the absence of infiltration testing and the traditional buried attenuation approach of the submitted strategy.

- The response report incorporates infiltration testing and concludes that it is not viable for this site.

- The revised proposal continues to exclude any SuDS source control due to spatial constraints. This is not acceptable in principle. This is a significant development with a substantial footprint. Space for water needs to be incorporated. Whilst ponds / basins may not be practicable. It is considered that features such as swales, tree-pits, raingardens, hydro-planters etc should be feasible.

- The discharge is proposed to be restricted to 71l/s (58% of the 30yr design runoff). This is not acceptable. Runoff should ideally be restricted to greenfield rates. If this is demonstrated to be unachievable then 50% of the Qbar runoff may be considered.

Drainage & Flood Officer Summary:

- Infiltration has been investigated and is not considered to be viable.

- The restricted discharge flowrate should ideally be greenfield or, if not feasible, then 50% of pre-development Qbar.

- The spatial excuses for excluding SuDS features and source controls are not acceptable, and it is considered the site should be able to incorporate some SuDS features.

- The above points should be addressed before the application can be approved.

Consultation by Keith Mealey

Drainage & Flooding Officer

keith.mealey@rochdale.gov.uk