|  |  | Public Health and Communities Kuiama Thompson Director of Public Health and Communities # Public Protection and Customers Number One Riverside, Smith Street, Rochdale, OL16 1XU Tel: (01706) 924688 Email: jonathon.parr@rochdale.gov.uk Website: www.rochdale.gov.uk |
| --- | --- | --- |

Date: 3rd June 2026

Team: Environmental Control (Landfill Gas)

Application Number: 25/00546/DOC

Proposal: Submission of details to comply with schedule 2 conditions 13 (Phasing Plan), 14 (FFL), 15 (Site Investigations), 16 (Coal Mining), 17 (Archaeology), 19 (Foul Drainage), 20 (Surface Water), 21 (CMS), 22 (CTMP), 23 (CEMP), 25 (LHCMP) and 28 (Water Main) on planning permission 16/01399/HYBR. Land Bound By Manchester Road, Hareshill Road And Pilsworth Road West Of Junction 19 Of The M62 Rochdale

Dear Nick,

I have reviewed the following information submitted as part of the application:

- GeoShield Drawing Perimeter Detail from Section A-A in drawing -200232_00043 REV 001, Drawing Numbers GEO106127-01-13

As per the guidance within BS 8485:2015+A1:2019, a Type D building (Large floor plan retail/commercial/industrial building at grade) requires a minimum score of 2.5.  I note that the applicants consultants, GeoShield are proposing the following:

- Juta TitanBond membrane which is resistant to hydrocarbons and prevent the migration of radon, carbon dioxide, and methane, and;

- Reinforced ground bearing slab above the membrane, as well as “foamed concrete” above the poured slab.

This provides a maximum of three points as per BS 8485:2015+A1:2019, which is acceptable.  Therefore, these drawings are sufficient.  I would hasten to add, we will require verification that the foundations have been constructed as per the design, so I would not recognise complete discharge of any condition yet.  This is covered by the following part of condition 15 of Schedule 2 on planning permission 16/01399/HYBR.

The development shall thereafter be carried out in full accordance with the duly approved remediation strategy and a verification report submitted to and approved in writing by the Local Planning Authority before any of the building(s) hereby approved are first occupied.

If you have any further queries, please do not hesitate to reach out.

Yours sincerely,

Jonathon Parr

Jonathon Parr

Environmental Health Senior Officer (Environment Prot)