# Highways and Engineering Service - Economy and Environment

# Drainage Consultation on Application – PL/2026/0610 – Greater Manchester Fire Station, Middleton Road, Heywood, OL10 2LU

LLFA Consultation Response on behalf of Head of Highways and Engineering

Date of Response: 3rd August 2026

Location & Proposed Development

Greater Manchester Fire Station, Middleton Road, Heywood, OL10 2LU

Two storey temporary fire station with an appliance bay to enable the continued operation of GMFRS during the redevelopment of the existing Fire Station

Documents Reviewed

- Existing Site Plan With Levels

- External Works Plan

- Outline Drainage Strategy

- Planning Statement

- Site Location Plan

Drainage & Flood Officer Comments

- The aim should be to discharge surface run off as high up the following hierarchy of drainage options as reasonably practicable: The ordered drainage techniques to be assessed with the aim to reduce or omit lower techniques:

- Control at Source (Infiltration / Recycling)

- On Site Treatment (Basins, Swales, Rain gardens, Tree pits)

- Local Treatment (Adoptable Ponds, Basins, Swales etc)

- Regional Treatment (ditto usually to a larger scale)

- Discharge to Watercourses / Bodies

- Discharge to SW Sewers

- Discharge to Combined Sewers

- The proposals are to re-use existing drainage surface water outfalls within the site. However, the current system has not been proven to an outfall ie watercourse or public sewer.

- The development is intended to be temporary and therefore it is considered that re-use of the current drainage is acceptable in principle provided that

- a reasonable estimate of the duration of the temporary works is provided.

- the permanent works incorporate a comprehensive assessment of the above hierarchy.

Drainage & Flood Officer Summary:

- The drainage proposals are acceptable in principle given that these are temporary works.

- An estimate for the temporary status / duration should be provided.

- The permanent works should infer no assumptions from the temporary works and undertake a comprehensive assessment of the SuDS hierarchy.

- The above points could be addressed by conditions.

Consultation by Keith Mealey

Drainage & Flooding Office

keith.mealey@rochdale.gov.uk