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Drainage Consultation on Application – OTH/2026/0660, 0661, 0662, 0664 - Trub Farm Manchester Road Rochdale OL11 2XG
LLFA Consultation Response on behalf of Head of Highways and Engineering
Date of Response: 29th September 2026
Location & Proposed Development
24/01007/FUL Trub Farm Manchester Road Rochdale OL11 2XG
Erection of 158 affordable dwellings including 2No three-storey apartment blocks, with associated access, car parking, private gardens, open space, play facilities, and landscaping, together with new pedestrian to Rochdale Canal towpath
OTH_2026_0660 DoC 11&14 
Submission of details to comply with conditions 11 (Finished Floor and External Ground Levels) and 14 (Phasing Plan) of planning permission 24/01007/FUL
The external works drawings submitted do not show any phasing or programme of works. It is assumed that drainage infrastructure such as the detention basin, drainage outfalls etc together with existing infrastructure diversions &/or protection works would be part of initial phases.
OTH_2026_0661, 0662 & 0664 DoC 12, 13, 28 & 29
Submission of details to comply with condition:
12 (Drainage Strategy) 
13 (Sewer Infrastructure) 
28 (Sewer Construction in the vicinity of the Rochdale Canal) 
29 (Culvert Protection Measures)
Documents Reviewed
· Previous LLFA Reviews11/06/2025, 20/02/2025 and 14/07/2025
· Flood Risk Assessment, ELLUC-MD-24018-FRA, rev F3 10/07/2025
· 20-01 Drainage Layout-20-01-01K
· 20-01 Drainage Layout-20-01-02L
Drainage & Flood Officer Comments
1. Significant liaison has been undertaken to deliver the current proposal. The suite of drawings across the 3 DoC applications remain consistent with the proposals from the last review 14/07/2025. However, several of the points from that review which were to be addressed at subsequent design stages have not been addressed.

2. It is considered that a revised FRA and Drainage Strategy should be submitted to incorporate a summary of the liaison for future reference perhaps as an addendum or appendix.

3. The drainage layouts should be revised to show an integrated / comprehensive incorporation for all drainage components and systems. The drawings still do not show how the raingardens are integrated within the system. This should be supported with hydraulic design calculations, contributing areas etc. It is unclear whether the hydraulic calculations previously submitted are still representative of the current design.

4. Some cover levels are similar to Finished Floor Levels (FFLs). FFLs should be 300mm above maximum flood levels. If the modelled flood levels are close to the surface, then this may not be achieved. It is noted the UU have also queried MH CLs relative to FFLs.

5. The drainage proposals should incorporate a Maintenance and Management plan for all components.

6. It is considered that a development of this magnitude should be supported by adopted drainage and highways infrastructure. Therefore, an adoption strategy should be provided. 

Drainage & Flood Officer Summary
i. A phasing plan clarifying how infrastructure will be provided should be submitted.
ii. A revised FRA&DS should be provided to capture the various liaison and design revisions.
iii. FFLs should be reviewed with respect to maximum flood levels.
iv. The adoption strategies should be clarified.
v. A Management and Maintenance Plan for all drainage components is required.
vi. If this is the final control point for these issues, then they should be addressed before the conditions are discharged. Alternatively, they could be addressed at subsequent stages if there are further controls (eg pre-occupation conditions etc).

Consultation by Keith Mealey
Drainage & Flooding Officer
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